## solar_plant
No. | Description | OID
1 | power out (MW) | 4222124688932872
2 | Average Cell Temp (deg C) | 4222125049970691 | **Average Cell Temp = (Cell Temp1+Cell Temp2) of Every zone / 8
3 | Average irradiance (W/m2) | 4222125050036227 |  | (Zone D, Zone E ถือเป็น 1 Zone เดียวกัน)
******Overall information***********
4 | Total DC Power (KW) | 4222124661014540 | **Ambient Temperature ถูกแก้ไขเป็น Cell Temperature ซึ่งเป็นค่าเดียวกับ
5 | Total Active Power (KW) | 4222124661080076 | หัวข้อ Meteorology ในแต่ละ Zone
6 | Total Reactive Power K(Var) | 4222124661276684
7 | Today Generating Capacity (kWh) | 4222124661145612
8 | Total Generating Capacity (MWh) | 4222124661211148
At Zone A
9 | Total DC Power (KW) | 4222125050101763
10 | Total Active Power (KW) | 4222125050167299
11 | Today Generating Capacity (kWh) | 4222125050232835
12 | Total Generating Capacity (MWh) | 4222125050298371
13 | Irradiance (W/m2) | 4222124903563272
14 | Ambient Temperature(deg C) | 4222124903366664
At Zone C
15 | Total DC Power (KW) | 4222125050626051
16 | Total Active Power (KW) | 4222125050691587
17 | Today Generating Capacity (kWh) | 4222125050757123
18 | Total Generating Capacity (MWh) | 4222125050822659
19 | Irradiance (W/m2) | 4222124903890952
20 | Ambient Temperature(deg C) | 4222124903694344
At Zone D
21 | Total DC Power (KW) | 4222125050888195
22 | Total Active Power (KW) | 4222125050953731
23 | Today Generating Capacity (kWh) | ToTotal
24 | Total Generating Capacity (MWh) | 4222124660686860
25 | Irradiance (W/m2) | 4222124904218631
26 | Ambient Temperature(deg C) | 4222124904022024
At Zone E
27 | Total DC Power (KW) | 4222124660752396
28 | Total Active Power (KW) | 4222124660817932
29 | Today Generating Capacity (kWh) | 4222124660883468
30 | Total Generating Capacity (MWh) | 4222124660949004
31 | Irradiance (W/m2) | 4222124904218631
32 | Ambient Temperature(deg C) | 4222124904022024
At Zone B
33 | Total DC Power (KW) | 4222125050363907
34 | Total Active Power (KW) | 4222125050429443
35 | Today Generating Capacity (kWh) | 4222125050494979
36 | Total Generating Capacity (MWh) | 4222125050560515
37 | Irradiance (W/m2) | 4222124904218631
38 | Ambient Temperature(deg C) | 4222124904022024
********Meteorology monitoing system***********
Zone A
38 | Environment temperature (deg C) | 4222124903366664
39 | Temperature 1 of solar panel (deg C) | 4222124903432200
40 | Temperature 2 of solar panel (deg C) | 4222124903825416
41 | Globe irradiation (W) | 4222124903563272
42 | Total globe irradiation (MJ) | 4222124903628808
Zone B
43 | Environment temperature (deg C) | 4222124904349703
44 | Temperature 1 of solar panel (deg C) | 4222124904415239
45 | Temperature 2 of solar panel (deg C) | 4222124904480775
46 | Globe irradiation (W) | 4222124904546311
47 | Total globe irradiation (MJ) | 4222124904611847
Zone C
48 | Environment temperature (deg C) | 4222124903694344
49 | Temperature 1 of solar panel (deg C) | 4222124903759880
50 | Temperature 2 of solar panel (deg C) | 4222124903825416
51 | Globe irradiation (W) | 4222124903890952
52 | Total globe irradiation (MJ) | 4222124903956488
Zone D
53 | Environment temperature (deg C) | 4222124904022024
54 | Temperature 1 of solar panel (deg C) | 4222124904087560
55 | Temperature 2 of solar panel (deg C) | 4222124904153095
56 | Globe irradiation (W) | 4222124904218631
57 | Total globe irradiation (MJ) | 4222124904284167
At G2 Relay
58 | P(MW) | 4222124703875083
59 | Q(MVar) | 4222124703940619
60 | Uab (kV) | 4222124702695438
61 | Ubc (kV) | 4222124702760975
62 | Uca (kV) | 4222124702826511
63 | F (Hz) | 4222124688605194
64 | Pf | 4222124689129479
65 | Ia(A) | 4222124702040078
66 | Ib(A) | 4222124702105614
67 | Ic(A) | 4222124702171150

## JSON
JSON Format: http://<host>/sp | [5 empty] | JSON Format: http://<host>/sr
{ | [5 empty] | {
| "plant" : | "Solar Plant" |  |  | <key> |  | "plant" : | "Solar Roof" |  |  | <key>
| "lastmodified" | "2016-08-31T16:45:00.000Z" |  |  |  |  | "lastmodified" | "2016-08-31T16:45:00.000Z"
| "data" : | [ |  |  |  |  | "data" : | [
|  |  | { | [5 empty] | {
|  |  |  | "oid": | "4222124661080076" |  |  |  |  | "oid": | 1
|  |  |  | "name": | "Total Active Power" |  |  |  |  | "name": | "Total Active Power"
|  |  |  | "value": | "2.5" |  |  |  |  | "value": | "2.5"
|  |  |  | "unit": | "KW" |  |  |  |  | "unit": | "KW"
|  |  | }, | [5 empty] | },
|  |  | { | [5 empty] | {
|  |  |  | … | [5 empty] | …
|  |  | } | [5 empty] | }
|  | ] | … | … |  |  |  | ] | … | …
} | [5 empty] | }
Example
http://<host>:2016/sp
{"plant":"Solar Plant","lastmodified":"2016-08-31T16:45:00.000Z","data":[{"oid":4222124660621324,"name":"Zone D:Today Generating Capacity","value":0,"unit":"KWh"},{"oid":4222124660686860,"name":"Zone D:Total Generating Capacity","value":27.824,"unit":"MWh"},{"oid":4222124660817932,"name":"Zone E:Total Active Power","value":0,"unit":"MWh"},{"oid":4222124660883468,"name":"Zone E:Today Generating Capacity","value":4251,"unit":"KWh"},{"oid":4222124660949004,"name":"Zone E:Total Generating Capacity","value":27.45,"unit":"MWh"},{"oid":4222124661080076,"name":"Total Active Power","value":0,"unit":"KW"},{"oid":4222124661145612,"name":"Today Generating Capacity","value":9456.3,"unit":"KWh"},{"oid":4222124661211148,"name":"Total Generating Capacity","value":151.126,"unit":"MWh"},{"oid":4222125049970691,"name":"Average Cell Temp","value":26.8,"unit":"deg C"},{"oid":4222125050036227,"name":"Average irradiance","value":0,"unit":"W/m2"},{"oid":4222125050167299,"name":"Zone A:Total Active Power","value":0,"unit":"MWh"},{"oid":4222125050232835,"name":"Zone A:Today Generating Capacity","value":0,"unit":"KWh"},{"oid":4222125050298371,"name":"Zone A:Total Generating Capacity","value":39.109,"unit":"MWh"},{"oid":4222125050429443,"name":"Zone B:Total Active Power","value":0,"unit":"MWh"},{"oid":4222125050494979,"name":"Zone B:Today Generating Capacity","value":5205.3,"unit":"KWh"},{"oid":4222125050560515,"name":"Zone B:Total Generating Capacity","value":23.727,"unit":"MWh"}]}
http://<host>:2016/sp/4222125050298371
{"oid":4222125050298371,"name":"Zone A:Total Generating Capacity","value":39.109,"unit":"MWh"}

## configuration
Data Flow Configuration
|  |  | RESTful API | Learning Center
| Solar Plant | Middleware Server | JSON | Server
| SCADA | Nodejs |  | PHP
|  | Express |  | Flash
| MySQL | Mongodb |  | MySQL
MEAN STACK
| Solar RoofTop |  | HTML/JSON
Text
Wind
???
Napia
???
update | 2016-09-29
BY | kongdej.s@egat.co.th
EIS
WEB
Mobile